Controlled Phase-Rectifiers: Semi-Converters, Full-Converters & Quadrant Inversion

Welcome to the VVDN Engineering Hub Technical Dossier on Controlled Phase-Rectifiers. Controlled rectifiers replace passive silicon diodes with Silicon-Controlled Rectifiers (SCRs / Thyristors) to provide variable, regulated DC voltage from an AC power grid.

Controlled rectifiers are the backbone of high-power DC motor drives (cranes, electric locomotives, rolling mills), battery charging stations, electrochemical chlor-alkali plants, and High-Voltage Direct Current (HVDC) transmission converter stations.

This guide provides an exhaustive hardware analysis covering single-phase and three-phase semi-converters and full-converters, firing delay angle α derivations, R-L-E load dynamics, and Quadrant IV Line-Commutated Inversion for regenerative braking.

1. Operating Principle & Rectifier Architectures

======================================================================================================================== DETAILED HARDWARE SCHEMATIC: SINGLE-PHASE FULLY-CONTROLLED THYRISTOR BRIDGE (230V AC -> 0-200V DC / 25A) ======================================================================================================================== AC LINE (230V RMS) ──[ F1: 30A Fast ]──┬─────────────────────────────────────────────────────────────┐ │ │ ┌┴┐ MOV1: 275V RMS │ │ │ (Surge Clamp) │ └┬┘ │ AC NEUTRAL ────────────────────────────┼───────────────────────────┬─────────────────────────────────┼───+ │ │ │ │ │ │ │ │ Anode (A) Anode (A) │ │ ┌────┴──────────┐ ┌────┴──────────┐ │ │ │ T1: THYRISTOR │ │ T3: THYRISTOR │ │ │ │ Vishay 40TPS12│ │ Vishay 40TPS12│ │ │ +----->│ (1200V, 35A) │ +----->│ (1200V, 35A) │ │ │ ¦ Gate └────┬──────────┘ ¦ Gate └────┬──────────┘ │ │ ¦ Cath │ ¦ Cath │ │ │ ¦ │ ¦ │ │ │ ¦ +---------------+-----------+=== COMMON CATHODE DC+ │ │ ¦ ¦ (0V to +207V Controlled) │ │ ¦ ¦ │ │ ¦ ├──[ R_snub: 22Ω / 5W ] +=== LOAD TERMINAL + │ │ ¦ │ │ ¦ │ │ ¦ │ [ C_snub: 0.1µF / 630V ] +---[ L_filter: 50mH / 25A ]--+ │ ¦ │ │ (DC Smoothing Choke) │ │ ¦ │ AC LINE │ │ ¦ │ │ │ ¦ Cath│ ┌─┴─┐ │ ¦ ┌────┴──────────┐ │ R │ │ ¦ │ T4: THYRISTOR │ │ L │ │ ¦ │ Vishay 40TPS12│ │ O │ │ ¦ +->│ (1200V, 35A) │ │ A │ │ ¦ ¦ └────┬──────────┘ │ D │ │ ¦ ¦ Anode│ └─┬─┘ │ ¦ ¦ │ │ │ ¦ ¦ +---------------------------+=== COMMON ANODE DC- │ │ ¦ ¦ ¦ (Return Reference) │ │ ¦ ¦ ¦ ┌┴┐ │ ¦ ¦ Cath│ │-│ │ ¦ ¦ ┌────┴──────────┐ │E│ │ ¦ ¦ │ T2: THYRISTOR │ │+│ │ ¦ ¦ │ Vishay 40TPS12│ └┬┘ │ ¦ ¦ +----->│ (1200V, 35A) │ │ │ ¦ ¦ ¦ Gate └────┬──────────┘ │ │ ¦ ¦ ¦ Anode│ (DC Motor Back-EMF) │ │ ¦ ¦ ¦ │ │ │ ¦ ¦ ¦ +─────────────────────────────────┼───+ ¦ ¦ ¦ │ │ +---¦-----------------------¦-----------¦---[ PULSE TRANSFORMER TX1: GATE 1 & 2 ] +-----------------------+-----------¦---[ PULSE TRANSFORMER TX2: GATE 3 & 4 ] │ (Isolated Trigger: 1:1, 100mA Firing Pulse) │ AC NEUTRAL ────────────────────────────────────────────────────────┴────────────────────────────────────────

1.1 Detailed Component Connection Netlist & Terminal Details:

| Net Name | Source (Pin / Terminal) | Destination (Pin / Terminal) | Electrical Function | Hardware Engineering Notes |
| --- | --- | --- | --- | --- |
| AC_LINE | AC Mains Live Feed | T_1 Anode, T_4 Cathode, Snubber | Input AC phase branch 1 | Line input connects between upper and lower thyristors of Leg 1. |
| AC_NEUTRAL | AC Mains Neutral Feed | T_3 Anode, T_2 Cathode, Snubber | Input AC phase branch 2 | Neutral connects between upper and lower thyristors of Leg 2. |
| DC_POS (+) | Thyristors T_1, T_3 Cathodes | DC Smoothing Choke L_filter Input | Controlled DC positive bus | Average DC voltage is V_dc = (2 V_m) / π cos α; can invert when α > 90°. |
| DC_NEG (-) | Thyristors T_4, T_2 Anodes | DC Motor / Load Negative Terminal | Controlled DC return rail | Commutated return carrying continuous unidirectional DC current. |
| GATE_1_4 | Pulse Transformer TX1 Secondary | Thyristors T_1, T_2 Gate-Cathode Pins | Synchronized gate firing pulse train | Fired simultaneously at angle α during positive utility half-cycle. |
| GATE_3_2 | Pulse Transformer TX2 Secondary | Thyristors T_3, T_4 Gate-Cathode Pins | Synchronized gate firing pulse train | Fired simultaneously at angle π + α during negative utility half-cycle. |

1.2 Component Bill of Materials & Parametric Specifications:

| RefDes | Component Description | Manufacturer & Part Number | Key Electrical Specifications | Critical Design Constraint |
| --- | --- | --- | --- | --- |
| T_1 ... T_4 | Phase-Control Thyristors | Vishay Semiconductors 40TPS12 | V_RRM = 1200 V, I_T(AV) = 35 A, I_GT = 150 mA, V_TM = 1.45 V | 1200 V rating easily withstands 325 V peak grid voltage plus motor back-EMF spikes. |
| R_snub, C_snub | Thyristor RC Snubbers | Ohmite 280 / KEMET PHE450 | R = 22 Ω / 5 W Wirewound, C = 0.1 µF / 630 V Film | Restricts rate of off-state voltage rise to dv / dt < 500 V/µs to prevent false dv/dt triggering. |
| TX_1, TX_2 | Gate Pulse Transformers | Pulse Electronics PE-64936 | Ratio: 1:1, V_isolation = 3000 V_RMS, E-T = 150 V*µs | Delivers sharp 150 mA, 10 µs firing pulses with steep rise time (< 100 ns). |
| L_filter | DC Smoothing Inductor | Hammond Mfg 195J25 | L = 50 mH, I_DC = 25 A, DCR = 85 mΩ | Heavy laminated iron core choke guarantees continuous conduction down to 5\% rated current. |

1.1 Semi-Converter vs. Full-Converter:

Semi-Converter (Single-Quadrant):

Consists of a mixture of diodes and SCRs (or includes a freewheeling diode).

Can only produce positive DC voltage and positive DC current (V_dc >= 0, I_dc >= 0).

Operates exclusively in Quadrant I (Power flows strictly from AC grid to DC load).

Offers superior input power factor and lower reactive power consumption than full converters.

Full-Converter (Two-Quadrant):

All switching elements are thyristors (4 SCRs for single-phase; 6 SCRs for three-phase).

Current is unidirectional (I_dc >= 0), but the average output DC voltage can be controlled continuously from positive to negative (-V_max <= V_dc <= +V_max) by varying firing angle α from 0° to 180°.

Operates in Quadrant I (Rectification) and Quadrant IV (Line-Commutated Inversion).

2. Operating Modes & Voltage Derivations

Full-Converter Output Voltage Waveforms Across Firing Angle v_out ^ Alpha = 30° (Rectification: Average Vdc > 0) │ /─\ /─\ /─\ 0V ┼──/───\─────/───\─────/───\───────────────────────────────────> Time │ \___/ \___/ \___/ (Vdc,avg is POSITIVE) v_out ^ Alpha = 90° (Zero Net Voltage: Vdc,avg = 0) │ /\ /\ /\ 0V ┼──/──\──────/──\──────/──\────────────────────────────────────> Time │ \ / \ / \ / (Positive and Negative Areas Equal!) │ \ / \ / \ / v_out ^ Alpha = 120° (Inversion: Average Vdc < 0) │ /--\ /--\ /--\ 0V ┼──/────\────/────\────/────\──────────────────────────────────> Time │ \__/ \__/ \__/ (Vdc,avg is NEGATIVE!)

2.1 Single-Phase Full-Converter Formulation:

For continuous load current with an inductive load (R-L):

V_dc,avg = 1 / π Integral(α to π + α) V_m sin(ω t) d(ω t) = V_m / π [ -cos(ω t) ]_α^π + α = (2 V_m) / π cos α

Where V_m = sqrt(2) * V_ac,rms.

α = 0°: V_dc = (2 sqrt(2)) / π V_ac,rms ≈ 0.90 * V_ac,rms (Maximum positive DC voltage).

α = 90°: V_dc = 0 V.

α > 90°: V_dc becomes strictly negative!

2.2 Three-Phase Six-Pulse Full-Converter Formulation:

The 6-pulse bridge conducts two thyristors simultaneously at any instant (one from top row, one from bottom row):

V_dc,avg = 3 / π Integral(π / 3 + α to 2π / 3 + α) v_LL(t) d(ω t) = (3 sqrt(2) * V_LL,rms) / π cos α ≈ 1.35 * V_LL,rms * cos α

2.3 Single-Phase Semi-Converter Formulation:

Because the diodes (or freewheeling diode) clamp the output voltage to 0 V whenever the AC line crosses zero, negative voltage excursions are prohibited:

V_dc,avg = 1 / π Integral(α to π) V_m sin(ω t) d(ω t) = V_m / π (1 + cos α) = (sqrt(2) V_ac,rms) / π (1 + cos α)

Notice that V_dc,avg >= 0 for all values of α (0 <= α <= π).

3. Quadrant IV: Line-Commutated Inversion & Regenerative Braking

In industrial DC motor drives (such as elevators, cranes, and electric trains), decelerating an inertia load generates back-EMF energy. A fully-controlled converter allows this mechanical kinetic energy to be converted into electrical power and pumped back into the AC utility grid.

Two-Quadrant Operation of Full-Converter +V_dc ^ │ QUADRANT II │ QUADRANT I: RECTIFICATION (Not Poss) │ (0° <= Alpha < 90°) │ Power: AC Grid -> DC Motor ──────────────┼─────────────────────────────> +I_dc │ QUADRANT III │ QUADRANT IV: INVERSION (Not Poss) │ (90° < Alpha < 180°) │ Power: DC Motor (Back-EMF) -> AC Grid -V_dc v (Regenerative Braking!)

3.1 Conditions for Inverter Operation:

Firing Angle Delay: Set α > 90° (typically α = 120° ... 150°). This makes the converter terminal voltage V_dc negative.

Reversed DC Source Polarity: The load DC source (motor back-EMF E or battery) must be connected with its polarity opposing the converter's forward conducting direction (E < 0).

Continuous Current: An inductor in series with the DC circuit ensures the current remains continuous.

Power Flow:

P = V_dc * I_dc = (-¦V_dc¦) * (+I_dc) < 0 (Power flows into the AC supply)

3.2 Commutation Failure Margin (γ):

A thyristor requires a finite turn-off recovery time (t_q ≈ 50 ... 200 µs) to recombine internal minority carriers before positive forward voltage is reapplied.

The extinction angle margin γ must satisfy:

γ = 180° - (α + u) >= ω * t_q

Where u is the commutation overlap angle caused by AC line source inductance L_s.

Disaster Hazard: If α is pushed too close to 180° (α > 165°), the incoming SCR fails to turn off before forward voltage returns. The bridge enters Commutation Failure, causing a catastrophic DC short circuit that trips high-speed fuses!

4. Input Power Factor & Reactive Power Consumption

A major hardware disadvantage of phase-controlled thyristor rectifiers is their high demand for reactive power (VAR) from the electrical utility grid:

Displacement Power Factor:

DPF = cos α

As the firing angle α increases to reduce output DC voltage (e.g., slowing down a DC motor), the phase displacement between input voltage and fundamental input current widens directly with α.

At α = 60°, DPF = cos(60°) = 0.50 lagging.

The utility must supply massive reactive power even when the active real power delivered to the motor shaft is small, incurring heavy power factor utility penalties.