Three-Phase DC-AC Inverters: 6-Switch VSI, THIPWM & Space Vector PWM (SVPWM)

Welcome to the VVDN Engineering Hub Technical Dossier on Three-Phase DC-AC Inverters. The three-phase Voltage Source Inverter (VSI) is the undisputed powerhouse of modern industrial motor drives (Variable Frequency Drives - VFD), Electric Vehicle (EV) traction inverters, high-power grid-connected solar farms, and wind power generation systems.

This guide provides an exhaustive mathematical and hardware analysis covering the two-level 6-switch VSI topology, six-step conduction modes, Third-Harmonic Injection PWM (THIPWM), and a masterclass deep dive into Space Vector Pulse-Width Modulation (SVPWM).

1. Operating Principle & 6-Switch VSI Topology

The three-phase two-level VSI comprises three identical half-bridge phase legs (Leg U, Leg V, Leg W) connected across a common stiff DC link:

======================================================================================================================== DETAILED HARDWARE SCHEMATIC: THREE-PHASE TWO-LEVEL VOLTAGE SOURCE INVERTER (VSI) (800V DC -> 400V 3-PHASE, 50kW) ======================================================================================================================== +VDC BUS (+800V Traction Battery / DC Link) ────────────────────────────────────────────────────────┐ │ │ ┌┴─────────────────┐ PHASE LEG U PHASE LEG V PHASE LEG W │ │ C_LINK_BULK │ Collector (C) Collector (C) Collector(C)│ │ 500µF / 900V │ ┌────┴──────────┐ ┌────┴──────────┐ ┌────┴──────┐│ │ Low-ESR Film │ │ Q1: HS LEG U │ │ Q3: HS LEG V │ │ Q5: HS W ││ │ (Laminated Bus) │ +----->│ Wolfspeed SiC │ +----->│ Wolfspeed SiC │ +->│ SiC MOSFET││ └┬─────────────────┘ ¦ Gate │ CAB016M12FM3 │ ¦ Gate │ CAB016M12FM3 │ ¦ │ 1200V/16mΩ││ │ ¦ └────┬──────────┘ ¦ └────┬──────────┘ ¦ └────┬──────┘│ │ ¦ Emitter│ ¦ Emitter│ ¦ Emit│ │ │ ISOLATED DRIVER ¦ │ ¦ │ ¦ │ │ │ UCC21750 (DESAT) ¦ +=== PHASE U (U) ¦ +=== PHASE V ¦ +=== PH W │ OUT_U_HS ---------+ ¦ (0V to +800V) ¦ ¦ (0V-800V)¦ ¦ (0V-800V) │ ¦ ¦ ¦ ¦ ¦ │ │ Collect(C) +-----------+ Collect(C) ¦ Collect(C) │ │ ┌────┴───────┴──┐ ┌────┴──────────┐ ¦ ┌────┴──────┐│ │ │ Q2: LS LEG U │ │ Q4: LS LEG V │ ¦ │ Q6: LS W ││ │ +----->│ CAB016M12FM3 │ +----->│ CAB016M12FM3 │ +->│ 1200V/16mΩ││ │ ¦ Gate └────┬──────────┘ ¦ Gate └────┬──────────┘ └────┬──────┘│ │ OUT_U_LS ---------+ Emitter│ OUT_V-+ Emitter│ OUT_W--+Emit│ │ │ (Low-Side Leg U) │ (Leg V Drivers) │ (Leg W Drivers) │ │ │ │ │ │ GND_DC ───────────────────────────────┴───────────────────────────────┴─────────────────────┴───────┴─── GND_DC │ │ │ │ INLINE HALL SENSORS │ │ ├──[ LEM CAB-500: Phase U ]─────┼─────────────────────┼───> TERMINAL U (Phase A) │ (Analog ADC -> TMS320F28379D)│ │ │ ├──[ LEM CAB-500 ]────┼───> TERMINAL V (Phase B) │ │ (Phase V Current) │ │ │ ├───> TERMINAL W (Phase C) │ │ │ │ │ +----------------------------+---------------------+ │ │ ¦ 3-PHASE LC OUTPUT SINE FILTER (OPTIONAL FOR GRID-TIE) │ │ ¦ - 3x Lf: 250µH / 100A Powder Core Chokes │ │ ¦ - 3x Cf: 22µF / 480VAC Delta-Connected Film Bank │ │ +----------------------------+---------------------+ │ │ │ │ │ +───────────────────────────────┼─────────────────────┼─────+ │ │ +========+=====================+=======+ ¦ 3-PHASE PERMANENT MAGNET SYNCHRONOUS¦ ¦ MOTOR (PMSM) / INDUCTION MACHINE ¦ +======================================+

1.1 Detailed Component Connection Netlist & Terminal Details:

| Net Name | Source (Pin / Terminal) | Destination (Pin / Terminal) | Electrical Function | Hardware Engineering Notes |
| --- | --- | --- | --- | --- |
| +VDC_BUS | EV Battery / DC Busbar | C_link (+), Q_1, Q_3, Q_5 Collectors/Drains | Main 800V DC high-voltage rail | Symmetrical planar laminated copper busbar minimizes stray parasitic inductance (L_stray < 15 nH). |
| PHASE_U (SW_U) | Q_1 Emitter, Q_2 Collector | Current Transducer CT_U, Motor Terminal U | Phase U high-power switching node | Swings between 0 V and +800 V at PWM carrier frequency f_c = 16 kHz ... 20 kHz. |
| PHASE_V (SW_V) | Q_3 Emitter, Q_4 Collector | Current Transducer CT_V, Motor Terminal V | Phase V high-power switching node | Displaced 120° electrically from Phase U; high dv/dt edge rates (> 20 V/ns). |
| PHASE_W (SW_W) | Q_5 Emitter, Q_6 Collector | Current Transducer CT_W, Motor Terminal W | Phase W high-power switching node | Displaced 240° electrically from Phase U; monitored by inline current transducer. |
| I_U / I_V / I_W | LEM CAB-500 Analog Outputs | DSP ADC Inputs (ADCIN_A0, A1, A2) | Instantaneous phase current feedback | Closed-loop Field Oriented Control (FOC / Clarke-Park transforms) requires < 1 µs sampling latency. |
| GND_DC | Q_2, Q_4, Q_6 Emitters, C_link (-) | DC negative return busbar | High-current power return | Continuous return busbar; isolated from 12V automotive control chassis ground. |

1.2 Component Bill of Materials & Parametric Specifications:

| RefDes | Component Description | Manufacturer & Part Number | Key Electrical Specifications | Critical Design Constraint |
| --- | --- | --- | --- | --- |
| Q_1 ... Q_6 | 3-Phase SiC Power Module | Wolfspeed CAB016M12FM3 | V_DS = 1200 V, I_D = 150 A, R_DS(on) = 16 mΩ | Half-bridge SiC module; ultra-fast body diode and low switching losses enable 98.8\% peak inverter efficiency. |
| C_link | DC Link Film Capacitor | KEMET C4AKJBW5500A3MJ | 500 µF, 900 V_DC, ESR = 1.2 mΩ, I_ripple = 85 A_rms | Handles severe triangular RMS ripple current drawn by 3-phase Space Vector PWM modulation. |
| U_drv1-6 | Isolated Smart Gate Drivers | TI UCC21750DW | 5.7 kV_RMS isolation, 10 A sink/source, integrated DESAT & AMC | Fast Overcurrent Desaturation (DESAT) shutdown (< 200 ns) protects SiC switches during phase short-circuits. |
| CT_U,V,W | Automotive Hall Current Sensors | LEM CAB 500-C/SP5 | ± 500 A primary range, 0.5\% accuracy, CAN / analog output | High galvanic isolation; measures DC and AC phase currents without inserting series resistance into motor cables. |
| U_ctrl | Central Motor Control MCU | TI TMS320F28379D | Dual-Core 32-bit floating-point C28x DSP, Trigonometric Math Unit | Computes Space Vector PWM (SVPWM) switching vectors V_0 ... V_7 in real-time every 50 µs. |

1.1 Switching Logic & Pole Voltages:

Each leg switch state can be defined by a binary variable S_x in {0, 1} (where x in {u, v, w}):

S_x = 1: High-side switch Q_high is ON; leg terminal voltage v_xN = V_dc.

S_x = 0: Low-side switch Q_low is ON; leg terminal voltage v_xN = 0 V.

2. Six-Step (180° & 120°) Conduction Modes

180-Degree Conduction Mode Phase Voltages Switch States: Q1 (Phase U) ───────┐ ┌───────────────────┐ └───────────────────────┘ └─────────────────── Q3 (Phase V) ───────────────┐ ┌───────────────────┐ └───────────────────────┘ └─────────── Q5 (Phase W) ───────────────────────┐ ┌───────────────────┐ ───────────────────────┘ └───────────────────┘ v_UN (Pole) +Vdc ──┐ ┌───────────────────┐ 0V ──┴───────────────────────┴───────────────────┴─────────────────── v_UV (Line) +Vdc ──────┐ ┌─── 0V ──────┴───────┐ │ -Vdc ──────────────┴───────┴─────────────────────────────────────────── │◄─ 60° ─►│ Six-Step Output (Severe 5th and 7th Harmonics!)

180° Conduction Mode: Exactly 3 switches are ON at any given instant. While generating maximum fundamental power, the output is a stepped six-step waveform with large low-order harmonics (5th, 7th, 11th), causing severe motor torque ripple and thermal losses.

Modern Drive Requirement: Variable frequency drives (VFD) and EV traction systems require high-frequency PWM to eliminate low-order harmonics.

3. Sinusoidal PWM vs. Third-Harmonic Injection (THIPWM)

3.1 Standard SPWM Limitation:

In standard SPWM, three sinusoidal reference waves shifted by 120° are compared against a common triangular carrier:

Linear modulation limit: m_a <= 1.0.

The maximum fundamental peak phase-to-neutral voltage is V_pk_ph = V_dc / 2.

The maximum RMS line-to-line voltage is:

V_LL,rms = (sqrt(3) * V_pk_ph) / sqrt(2) = (sqrt(3) * V_dc) / (2 sqrt(2)) ≈ 0.612 * V_dc

Problem: Almost 39\% of the available DC-bus voltage capability is wasted!

3.2 Third-Harmonic Injection (THIPWM):

By injecting a third harmonic with an amplitude of 1 / 6 of the fundamental into each phase reference:

v_ref,u(t) = V_pk_1 sin(ω t) + 1 / 6 V_pk_1 sin(3ω t)

Third-Harmonic "Saddle" Waveform & DC Expansion v_ref ^ │ Saddle Shape (Peak Voltage Reduced by 15.5%!) │ .-'""'-. .-'""'-. │ / \ / \ 0V ┼─────────/──────────\───/──────────\──────────────────────────> Time │ '-' '-' │◄──────────────── Third-Harmonic Injected ────────────────►│

The third harmonic flattens the crest of the sinusoidal reference wave ("saddle shape"), preventing the peak from touching the triangular carrier limits.

Because the three phases are identical, the third-harmonic components cancel out completely in the line-to-line differential voltages (v_uv = v_u - v_v).

The Result: Maximum modulation index increases from m_a = 1.0 to m_a = 2 / sqrt(3) ≈ 1.155 without entering non-linear overmodulation, boosting AC output voltage by 15.5\%!

4. Space Vector PWM (SVPWM) Masterclass

Space Vector PWM (SVPWM) is the mathematical and industrial pinnacle of inverter modulation, providing optimal harmonic cancellation and maximizing DC bus utilization.

4.1 Clarke Transformation to the Stationary α-β Frame:

The three instantaneous phase voltages are mapped onto a two-dimensional orthogonal complex plane:

begin{bmatrix} v_α \\ v_β end{bmatrix} = 2 / 3 begin{bmatrix} 1 & -1 / 2 & -1 / 2 \\ 0 & sqrt(3) / 2 & -sqrt(3) / 2 end{bmatrix} begin{bmatrix} v_u \\ v_v \\ v_w end{bmatrix}

4.2 The Eight Voltage Space Vectors:

With 3 switch legs and 2 states per leg (S_u, S_v, S_w), there are 2^3 = 8 possible switching combinations:

The SVPWM Hexagon and 8 Space Vectors +V_beta ^ │ V3 (010) │ V2 (110) \ │ / \ SEC 2 │ SEC 1 / \ │ / \ │ V_ref / Angle θ \ │ .---' \ │ / / V4 (011) ───────\─────┼─────/─────── V1 (100) ───> +V_alpha / │ \ Magnitude = (2/3)*Vdc / │ \ / SEC 3 │ SEC 6 \ / │ \ / SEC 4 │ SEC 5 \ / │ \ V5 (001) │ V6 (101) │ Zero Vectors: V0 (000) & V7 (111) at origin

Six Active Vectors (V_1 ... V_6):

Each vector has a magnitude of 2 / 3 V_dc and is separated from its neighbors by 60°, forming the vertices of a regular hexagon.

V_1(100): θ = 0°

V_2(110): θ = 60°

V_3(010): θ = 120°

V_4(011): θ = 180°

V_5(001): θ = 240°

V_6(101): θ = 300°

Two Zero Vectors (V_0, V_7):

V_0(000): All three low-side switches are ON; phase terminals shorted to GND.

V_7(111): All three high-side switches are ON; phase terminals shorted to +V_dc.

Magnitude is identically 0 Volts.

5. Dwell Time Formulations & Symmetric Switching

To synthesize an arbitrary rotating reference voltage vector vec{V}_ref at angle θ inside Sector 1 (0 <= θ <= 60°), the inverter time-averages the two adjacent active vectors (V_1, V_2) and the zero vectors (V_0, V_7) over switching period T_s:

vec{V}_ref * T_s = vec{V}_1 * T_1 + vec{V}_2 * T_2 + vec{V}_z * T_0

5.1 Dwell Time Equations for Sector 1:

T_1 = sqrt(3) * T_s * ¦vec{V}_ref¦ / V_dc * sin(π / 3 - θ)

T_2 = sqrt(3) * T_s * ¦vec{V}_ref¦ / V_dc * sin(θ)

T_0 = T_s - T_1 - T_2

(Where T_0 is divided equally between zero states V_0 and V_7: T_V0 = T_V7 = T_0 / 2.)

5.2 Symmetric 7-Segment Switching Sequence:

To minimize semiconductor switching losses and generate zero-crossing odd harmonic cancellation, the switching sequence in Sector 1 is structured symmetrically:

Symmetric 7-Segment Switching Pattern (Sector 1) State: │ V0 (000) │ V1 (100) │ V2 (110) │ V7 (111) │ V2 (110) │ V1 (100) │ V0 (000) │ │◄─ T0/4 ───►│◄─── T1/2 ─►│◄─── T2/2 ─►│◄─── T0/2 ─►│◄─── T2/2 ─►│◄─── T1/2 ─►│◄─ T0/4 ───►│ Leg U: ─────────────────┌────────────────────────────────────────────────────────┐───────────────── (Su) ─────────────────┘ └───────────────── Leg V: ──────────────────────────────┌──────────────────────────────┐────────────────────────────── (Sv) ──────────────────────────────┘ └────────────────────────────── Leg W: ───────────────────────────────────────────┌────┐─────────────────────────────────────────── (Sw) ───────────────────────────────────────────┘ └─────────────────────────────────────────── │◄──────────────────────────────── Switching Period Ts ────────────────────────────────────►│

Key Engineering Features of 7-Segment SVPWM:

Single-Leg Toggling: At every state transition, only one phase leg changes state (0 -> 1 or 1 -> 0), minimizing switching losses.

Maximum Linear AC Output: The maximum radius of the reference vector corresponds to the inscribed circle of the hexagon:

¦vec{V}_ref,max¦ = 2 / 3 V_dc * cos(30°) = V_dc / sqrt(3) ≈ 0.577 * V_dc

The resulting maximum fundamental line-to-line RMS voltage is:

V_LL,rms = (sqrt(3) * ¦vec{V}_ref,max¦) / sqrt(2) = V_dc / sqrt(2) ≈ 0.707 * V_dc

SVPWM achieves a full 15.5\% increase in AC output voltage over standard sinusoidal SPWM (0.707 vs. 0.612)!

Harmonic Cancellation: Center-aligned symmetric PWM eliminates all even harmonics and significantly reduces total harmonic distortion (THD).