Active Power Factor Correction (PFC) Rectifiers: Boost, Totem-Pole GaN & Vienna

Welcome to the VVDN Engineering Hub Technical Dossier on Active Power Factor Correction (PFC) Rectifiers. To comply with international grid harmonic regulations (IEC 61000-3-2 Class D and IEEE 519), every offline power supply exceeding 75\,W—from server power supplies and laptop adapters to EV on-board chargers and telecom rectifiers—must incorporate Active PFC.

This guide provides an exhaustive hardware engineering analysis of the classic Active Boost PFC Pre-regulator, the ultra-high-efficiency Bridgeless Totem-Pole GaN PFC, and the multi-megawatt Three-Phase Three-Level Vienna Rectifier.

1. Why Active PFC? Regulatory Mandates & Power Quality

A passive diode rectifier draws narrow current spikes, resulting in poor power factor (PF \approx 0.60) and massive harmonic injection (THD_i > 80\%).

Passive Diode Current vs. Active PFC Current Waveforms PASSIVE RECTIFIER: ACTIVE PFC RECTIFIER: v_in, i_in ^ v_in, i_in ^ │ Pulsed Current Spikes │ Input Current i_in is pure SINUSOID │ ¦ ¦ │ in PERFECT PHASE with Voltage v_in! │ / \ / \ │ /\ /\ │ .---' '---. .---' '---. │ .---./ \.-. .---./ \.-. │ / Voltage \ / │ / / \ \ / / \ \ 0V ┼/───────────────\─────────/──> Time 0V ┼/────/──────\──\────/──────\──\──> Time │ PF = 0.60, THDi = 110% │ PF = 0.998, THDi = 2.5% │ (FAILS IEC 61000-3-2) │ (COMPLIES WITH IEC 61000-3-2 CLASS D)

True Power Factor Decomposition:

\text{PF} = \frac{\text{Real Power } (P)}{\text{Apparent Power } (S)} = \frac{1}{\sqrt{1 + \text{THD}_i^2}} \cdot \cos \phi_1

To achieve PF \approx 1.0, the power supply must concurrently:

Drive phase displacement angle to zero (\cos \phi_1 \rightarrow 1.0).

Force harmonic distortion to near zero (THD_i \rightarrow 0 \implies \frac{1{\sqrt{1 + THD_i^2 \rightarrow 1.0).

2. Classic Active Boost PFC Topology & Dual-Loop Control

The standard Active Boost PFC cascades a full-wave diode bridge with a high-frequency step-up boost converter:

======================================================================================================================== DETAILED HARDWARE SCHEMATIC: CONTINUOUS CONDUCTION MODE (CCM) ACTIVE BOOST PFC (85V-265V AC -> 400V DC, 600W) ======================================================================================================================== AC LINE (85-265V) ──[ F1: 8A Time-Lag ]──[ NTC: 5Ω/8A ]──┬──[ EMI FILTER ]──[ BRIDGE RECTIFIER ]──┬─────────────────┐ (Relay K1 Bypass)│ (CX1, CMC1, CY1) (GBU808: 800V/8A) │ │ AC NEUTRAL ────────────────────────────────────────────────┴──────────────────────────────────────┼─┐ │ │ │ │ +-----------------[ D_inrush: 10A / 600V Standard ]---------------+ │ │ ¦ (Direct Startup Inrush Bypass Path) │ │ ¦ │ │ ¦ │ │ ¦ PFC BOOST INDUCTOR │ │ ¦ +---[ L_pfc: 450µH / 8A ]---------+ │ ¦ ¦ Sendust CS33125 Toroid │ │ ¦ ¦ (DCR = 45mΩ, Isat = 11A) ┌┴┐ C_in_HF │ ¦ +----------------+ │ │ 1.0µF / 450V │ ¦ │ └┬┘ Poly Film │ ¦ +=== NODE SW │ (Absorbs HF) │ ¦ ¦ (0V to 400V)│ │ ¦ ¦ │ │ ¦ Drain (D) ├──[ R_snub ] │ │ ¦ ┌────┴──────────┐ │ 2.2Ω / 2W │ │ ¦ │ Q1: N-MOSFET │ │ [ C_snub ] │ │ ¦ │ IPW60R045CP │ │ 470pF/630V │ │ ¦ +----->│ (650V, 45mΩ) │ │ GND_PWR │ │ ¦ ¦ Gate └────┬──────────┘ │ │ │ ¦ ¦ Source│ │ │ │ ¦ GATE DRIVER IC ¦ │ │ │ │ ¦ UCC27517 (Low-Side) ¦ +--------------+ │ │ ¦ OUT ----[ R_g: 4.7Ω ]+ │ │ │ ¦ ┌┴┐ R_shunt: 20mΩ / 3W 1% │ │ ¦ │ │ (Low-Side Inductor Sense) │ │ ¦ └┬┘ │ │ ¦ │ │ │ ¦ GND_PWR ───────────────────────────┴───────────────┘ ¦ │ ¦ BOOST PFC RECTIFIER DIODE │ ¦ +---[ D_pfc: SiC Schottky ]--+ ¦ ¦ Wolfspeed C3D06060A ¦ ¦ (600V, 6A, Qrr = 0) ¦ +---[ Anode ->¦ Cath ]-----+ ¦ │ +───────────────────────────────────+=== +VDC BUS (+400V DC Regulated) │ ┌┴──────────────────┐ │ C_BULK BANK │ ┌┴┐ 2x 330µF / 450V ┌┴┐ C_HF_CER │ │ Nichicon LGN │ │ 2x 0.47µF / 630V └┬┘ (Hold-Up Cap) └┬┘ Film Capacitor │ │ │ +VDC │ │ │ │ │ [ R_fb1: 1.0MΩ / 0.5W ] │ [ R_fb2: 1.0MΩ / 0.5W ] │ │ │ +---> V_FB (To PFC Controller) │ │ (V_ref = 2.500V) │ [ R_fb3: 12.7kΩ / 0.1% ] │ │ │ AGND (Quiet Ground) │ │ │ (Single Star Tie Point) GND_PWR (Power Ground Return) ─────────────────────────────────────┴────────+──────────┴───> -VDC (GND)

2.1 Detailed Component Connection Netlist & Terminal Details:

| Net Name | Source (Pin / Terminal) | Destination (Pin / Terminal) | Electrical Function | Hardware Engineering Notes |
| --- | --- | --- | --- | --- |
| RECT_OUT (+) | Full-Wave Bridge (+) | Inrush Diode D_{inrush Anode, Boost Choke L_{pfc Pin 1, C_{in,HF | 100Hz/120Hz rectified haversine input | High-frequency film cap C_{in,HF prevents 100kHz ripple from feeding back into bridge diodes. |
| SW (PFC Node) | Boost Choke L_{pfc Pin 2, Q_1 Drain | SiC Diode D_{pfc Anode, Snubber | High-voltage 100kHz boost switching node | Heavy trace routing; minimize loop area between Q_1 drain, D_{pfc anode, and C_{bulk return. |
| +VDC (400V Bus) | Diode D_{pfc Cathode, D_{inrush Cathode | C_{bulk bank (+), Feedback Divider, Downstream PSU | Regulated +400V DC intermediate bus | Inrush diode D_{inrush bypasses boost choke during plug-in to prevent core saturation. |
| ISENSE_P / N | Current Shunt R_{shunt Kelvin Pads | PFC Controller Current Loop Amplifier | Average inductor current sensing | Route as shielded differential pair; carries rectified sinusoidal current wave. |
| V_FB | Resistor Divider R_{fb1-3 Junction | PFC Controller Voltage Loop Amp (Pin 1) | Output voltage regulation feedback | Total divider resistance \approx 2\,M\Omega to minimize quiescent bleeder power dissipation. |
| GND_PWR | Bridge (-), R_{shunt (-), C_{bulk (-) | High-current power return plane | Circulating power stage ground | Solid ground plane; isolated from quiet analog signal ground AGND. |

2.2 Component Bill of Materials & Parametric Specifications:

| RefDes | Component Description | Manufacturer & Part Number | Key Electrical Specifications | Critical Design Constraint |
| --- | --- | --- | --- | --- |
| $Q_1$ | PFC Boost N-MOSFET | Infineon IPW60R045CP | V_{DS = 650\,V, I_D = 60\,A, R_{DS(on) = 45\,m\Omega, Q_g = 150\,nC | Superjunction CoolMOS provides ultra-low conduction losses at high RMS current (I_{rms \approx 6.5\,A at 90\,V_{ac). |
| $D_{pfc}$ | SiC Boost Rectifier Diode | Wolfspeed C3D06060A | V_{RRM = 600\,V, I_F = 6\,A, Q_c = 14\,nC, V_F = 1.5\,V | Zero Reverse Recovery ($Q_{rr} \approx 0$): Essential for continuous conduction mode (CCM) to avoid turn-on shoot-through. |
| $D_{inrush}$ | Startup Inrush Bypass Diode | Diodes Inc. S10MC | V_{RRM = 1000\,V, I_F = 10\,A, I_{FSM = 300\,A | Conducts initial 80\,A surge at AC plug-in; prevents L_{pfc saturation and protects D_{pfc. |
| $L_{pfc}$ | Boost PFC Inductor | Custom Sendust Core (CS33125) | L = 450\,µH, I_{sat = 11\,A, I_{rms = 7.5\,A, DCR = 45\,m\Omega | Low-permeability Sendust material (µ_r = 60) maintains soft saturation characteristics without overheating. |
| $C_{bulk}$ | DC Bus Bulk Capacitors | Nichicon LGN2W331MELY | 2 × 330\,µF, 450\,V_{DC, 105^\circC, ESR = 0.18\,\Omega | Accommodates 100Hz double-frequency ripple current (I_{ripple \approx 2.8\,A_{rms) and 20ms hold-up. |
| $R_{shunt}$ | Inductor Current Sense Shunt | Isabellenhütte ISA-WELD | 20\,m\Omega, 3.0\,W, 1\%, TCR < 20\,ppm/^\circC | Non-inductive electron-beam welded manganin construction ensures clean current measurement. |
| $U_1$ (PFC IC) | CCM PFC Controller | TI UCC28019A / UCC28180 | Continuous average current mode, internal ramp sync | Eliminates external AC voltage sensing; requires only current and output voltage sense. |

2.1 The Boost Requirement (V_{dc = 400\,V):

Because a Boost converter can only step up voltage (V_{out > V_{in), the regulated DC bus must exceed the peak of the highest AC input line voltage:

Universal AC Mains: 85\,V \dots 265\,V_{rms

Maximum Peak AC Line: V_{pk,max = \sqrt{2 \cdot 265\,V \approx 375\,V

Standard Industry DC Bus: $V_{dc} = 390\,\text{V} \dots 400\,\text{V}$ DC.

2.2 Dual-Loop Average Current-Mode Control:

Dual-Loop Average Current-Mode Controller 400V DC Bus │ [ Voltage Divider ] │ v V_fb V_ref (2.5V) ──────>( - ) │ [ Error Amp 1 ]<┘ (Voltage Loop) │ v V_comp (Slow Outer Loop: ~10 Hz Bandwidth) ¦v_in(t)¦ │ (Rectified Sine) ────────────( X ) MULTIPLIER │ v i_ref(t) = k * V_comp * ¦v_in(t)¦ (Reference Current) │ v ┌─────( - ) │ [ Error Amp 2 ] (Inner Fast Current Loop: ~15 kHz) │ │ │ v │ [ PWM Modulator ] ───> Gate Q1 (100 kHz) │ ^ │ │ Inductor Current i_L ──┴──────┘

Slow Outer Voltage Loop ($\sim 10 \dots 20\,\text{Hz}$):

Compares the 400\,V DC bus with a reference to maintain voltage regulation.

Crucial Engineering Rule: The loop bandwidth must be strictly below 20\,Hz to avoid tracking the 100\,Hz / 120\,Hz rectified AC line ripple. If the voltage loop were fast, it would distort the input current reference!

Fast Inner Current Loop ($\sim 10 \dots 20\,\text{kHz}$):

Multiplies the voltage error signal V_{comp by the instantaneous rectified AC line waveform |v_{in(t)| to construct an instantaneous reference current i_{ref(t).

Modulates the switch duty cycle cycle-by-cycle to force the inductor current i_L(t) to perfectly match i_{ref(t).

3. Advanced Bridgeless Totem-Pole GaN PFC

Conventional Boost PFC suffers conduction losses from the diode bridge (2 × V_F \approx 2 × 0.8\,V = 1.6\,V drop \implies 16\,W lost at 10\,A). The Bridgeless Totem-Pole PFC eliminates the diode bridge entirely:

Bridgeless Totem-Pole PFC Power Stage L_pfc AC Line ───────────^^^^^^──────┬───────────────────────────────┐ │ │ Drain (D) Drain (D) ┌───┴───┐ Q1 (GaN HEMT) ┌───┴───┐ S1 (Si Superjunction) │ HS │ High-Frequency │ LS │ Low-Frequency └───┬───┘ (100kHz - 1MHz) └───┬───┘ Line Synchronous │ Source │ Source (50Hz) ├── Midpoint HF ──┐ ├── Midpoint LF ──┐ │ │ │ │ Drain (D) │ Drain (D) │ ┌───┴───┐ Q2 (GaN HEMT)│ ┌───┴───┐ S2 (Si Superjunction) │ LS │ High-Frequency│ │ LS │ Low-Frequency └───┬───┘ (100kHz - 1MHz)│ └───┬───┘ Line Synchronous │ Source │ │ Source (50Hz) │ GND_DC ────────────────────────┴─────────────────┼─────────────┴─────────────────┼─── GND_DC │ │ AC Neutral ──────────────────────────────────────┼───────────────────────────────┘ │ ┌┴┐ C_bulk (400V DC) │ │ └┬┘

3.1 Why Silicon MOSFETs Fail in Totem-Pole (The GaN Revolution):

In the totem-pole configuration, the high-frequency switches operate in continuous conduction mode (CCM) half-bridge hard switching.

Standard silicon MOSFETs possess massive body-diode reverse recovery charge (Q_{rr \approx 500 \dots 2000\,nC). When the opposite switch turns ON, this Q_{rr causes destructive shoot-through spikes and extreme switching losses.

Gallium Nitride (GaN) HEMTs have ZERO reverse recovery ($Q_{rr} = 0\,\text{nC}$).

GaN enables the Totem-Pole topology to operate in CCM at > 100\,kHz, achieving unprecedented $99.2\%$ conversion efficiency!

4. Three-Phase Three-Level Vienna Rectifier

For high-power EV DC fast charging stations (50\,kW \dots 350\,kW) and megawatt data centers, the Vienna Rectifier is the premier unidirectional active PFC topology:

Three-Phase Three-Level Vienna Rectifier L1 Phase A ───────^^^^^──┬───[>¦]─┬───[>¦]─────────────────────────────┬───> +400V (Vdc/2) │ D1 │ D2 │ ├──[~]───┤ ┌┴┐ │ Q1 │ Bidirectional │ │ C1 │ (MOS) │ Midpoint Switch └┬┘ │ │ ├─── Neutral (0V) ├──[¦<]──┴───[¦<]─────────────────────────┐ │ │ D3 D4 │ ┌┴┐ │ │ │ │ C2 └──────── Neutral Midpoint (0V) ──────────┼──└┬┘ │ │ └───┴───> -400V (-Vdc/2) Total Vdc = 800V

Key Engineering Advantages:

Three-Level Voltage Synthesis: Node voltages switch between +\frac{V_{dc{2, 0\,V, and -\frac{V_{dc{2.

Halved Switch Voltage Stress: Each MOSFET switch Q_1 experiences only half the total DC-link voltage (400\,V stress on an 800\,V EV bus!), allowing the use of low-cost, ultra-fast 650\,V Superjunction or GaN FETs instead of expensive 1200\,V SiC modules.

Pristine Grid Quality: Inherent 3-level PWM cuts inductor ripple in half, achieving THD_i < 2.0\% and PF > 0.998.

5. Component Sizing & Bulk Capacitor Hold-Up Time

5.1 Inductor Sizing (L_{pfc):

Worst-case ripple occurs at the peak of the minimum AC line voltage:

L_{pfc} \ge \frac{V_{in,pk,min} \cdot \left( 1 - \frac{V_{in,pk,min}}{V_{dc}} \right)}{f_s \cdot \Delta I_L}

Where V_{in,pk,min = \sqrt{2 \cdot 85\,V \approx 120\,V, V_{dc = 400\,V, and \Delta I_L = 20\% \cdot I_{pk,max.

5.2 Bulk Capacitor Sizing for Hold-Up Time (t_{hold):

Server and telecom specifications (e.g., Intel ATX / Open Compute) mandate that the DC bus must sustain full output power during a complete AC line dropout of 1 \dots 2 missing AC cycles (t_{hold = 16.67\,ms \dots 20\,ms) without V_{dc falling below the downstream DC-DC converter's minimum drop-out threshold (V_{dc,min \approx 300\,V):

\Delta E = P_{out} \cdot t_{hold} = \frac{1}{2} C_{bulk} \left( V_{dc,nom}^2 - V_{dc,min}^2 \right)

C_{bulk} \ge \frac{2 \cdot P_{out} \cdot t_{hold}}{\eta \cdot \left( V_{dc,nom}^2 - V_{dc,min}^2 \right)}

Practical Sizing Example (1000\,W Server PSU):

P_{out = 1000\,W, \eta = 0.95

V_{dc,nom = 400\,V, V_{dc,min = 300\,V

t_{hold = 20\,ms (0.020\,s)

C_{bulk} \ge \frac{2 \cdot 1000 \cdot 0.020}{0.95 \cdot (400^2 - 300^2)} = \frac{40}{0.95 \cdot (160000 - 90000)} = \frac{40}{66500} \approx 601\,\mu\text{F}

Design Recommendation: Specify two 330\,µF / 450\,V (660\,µF total) high-temperature 105^\circC aluminum electrolytic capacitors in parallel.