EVSE Architecture & IoT Low Voltage Controller Knowledge Base

Welcome to the VVDN EVSE (Electric Vehicle Supply Equipment) Knowledge Base. This repository provides an end-to-end engineering guide to the architecture, electrical design, firmware state machines, safety interlocks, and IoT connectivity of Low Voltage (LV) Controller Boards used in modern AC Smart Chargers and DC Fast Charging systems.

1. Executive Summary & System Division

In modern Electric Vehicle Supply Equipment (EVSE), the hardware is divided into two distinct electrical domains:

High Voltage (HV) / Power Distribution Stage: Manages the grid AC input (Single-Phase 230\,V or Three-Phase 400\,V), main contactors, heavy-gauge busbars, residual current sensors, and high-power relays.

Low Voltage (LV) Controller Board (The "Brain" & IoT Gateway): Operates strictly within the Safety Extra Low Voltage (SELV / PELV) domain (typically +12\,V, +5\,V, and +3.3\,V). It executes vehicle pilot signaling, contactor actuation, safety monitoring, precision energy metering, user authentication, and cloud communication over OCPP.

HIGH VOLTAGE DOMAIN (230V / 400V AC) LOW VOLTAGE CONTROLLER DOMAIN (SELV) ┌───────────────────────────────────────────────┐ ┌─────────────────────────────────────────────────┐ │ │ │ │ │ AC Grid In ──────► Main Contactor ─────► EV │ │ Microcontroller (Real-Time Safety & Pilot) │ │ (L1, L2, L3, N) ▲ │ │ • IEC 61851-1 Control Pilot (±12V PWM) │ │ │ (12V Coil Drive) │ │ • Proximity Pilot (Cable Rating Sensing) │ │ │ │ │ • Contactor Coil Driver & Auxiliary Feedback │ │ Current Transformers ───┼────────────────────┼────►│ • 6mA DC / 30mA AC Residual Current Monitor │ │ (Energy Metering) │ (Opto-Isolated) │ │ • Energy Metering AFE (CS5463 / ADE7953) │ │ │ │ │ • Motorized Connector Lock H-Bridge │ │ Auxiliary SMPS │ │ ├─────────────────────────────────────────────────┤ │ (85-264V AC to 12V DC)──┼────────────────────┼────►│ IoT Gateway & Communications Processor │ │ │ │ │ • Wi-Fi (802.11 b/g/n) & BLE 5.0 │ │ Protective Earth (PE) ──┴────────────────────┼────►│ • 4G LTE Cat-1 / NB-IoT Cellular Modem │ │ │ │ • Ethernet (10/100 Mbps RJ45) │ │ │ │ • RS-485 Modbus (Dynamic Load Balancing) │ │ │ │ • RFID / NFC Tap (ISO 14443 Type A/B) │ │ │ │ • OCPP 1.6-J / OCPP 2.0.1 Cloud Stack │ └───────────────────────────────────────────────┘ └─────────────────────────────────────────────────┘

2. Core Functional Blocks of the LV Controller Board

The IoT-based Low Voltage Controller Board integrates nine critical electronic subsystems:

Power Management Unit (PMU): Converts the auxiliary +12\,V/+24\,V input from the main power board into stable +5\,V, +3.3\,V, and generating a precision ± 12\,V dual-rail supply for the Control Pilot. Includes a supercapacitor "Last-Gasp" backup circuit to dispatch power-failure alerts to the cloud before shutting down.

Control Pilot (CP) Circuit: Implements the ± 12\,V, 1.0\,kHz bipolar PWM signaling specified by IEC 61851-1 and SAE J1772. Modulates duty cycle to communicate available current (6\,A to 80\,A) and samples pilot voltage via precision op-amps to detect vehicle state changes (States A, B, C, D, E, F).

Proximity Pilot (PP) & Cable Detect: Senses the resistor-encoded value of the connected Type 2 charging cable (13\,A, 20\,A, 32\,A, 63\,A) and controls a motorized solenoid H-bridge to physically lock the plug into the socket during an active session.

Safety & Protective Interlocks:

Residual Current Monitoring (RCM): Interfaced to an active fluxgate sensor detecting 6\,mA DC and 30\,mA AC leakage currents (IEC 62955 compliance).

Welded Contactor Detection: Optocoupled or auxiliary contact sensing ensuring main contacts open cleanly before the plug lock releases.

Open Protective Earth (PE) Monitoring: Continuously monitors the chassis ground bond and neutral-to-earth potential.

Over-Temperature Monitoring: Analog NTC thermistors placed on high-current terminals, contactor body, and the PCB ambient.

Hardware Emergency Stop (E-Stop): Fail-safe hardware trip cutting off contactor gate drive instantly.

Precision Energy Metering: An integrated Analog Front-End (AFE) measuring True RMS Voltage, True RMS Current, Active Power, Reactive Power, and Total Active Energy (kWh) compliant with MID (European Measuring Instruments Directive).

Contactor Actuation Driver: Low-side N-channel MOSFET or smart high-side driver with inductive flyback suppression diode to switch the 12\,V or 24\,V DC coils of 4-pole power contactors.

Human-Machine Interface (HMI): High-luminance RGB LED halo/ring (displaying Ready, Authorizing, Charging, and Fault modes), piezo audio buzzer, and high-frequency RFID/NFC reader (13.56 MHz) for user tap-to-charge authentication.

IoT Network Gateway: Dual-processor (Cortex-M4 safety MCU + Linux/FreeRTOS IoT SoC) or integrated wireless SoC (e.g., ESP32-S3 / NXP i.MX) supporting multi-bearer connectivity (Wi-Fi, Bluetooth, 4G LTE, Ethernet).

Cloud Protocol Engine (OCPP 1.6-J & 2.0.1): Runs secure WebSockets (wss://) with TLS 1.3 to communicate with the Central System / Charging Station Management System (CSMS).

3. Applicable Industry & Safety Standards

| Standard | Governing Body | Scope & Application in EVSE |
| --- | --- | --- |
| IEC 61851-1 | International Electrotechnical Commission | General requirements for conductive EV charging systems, pilot functions, sequencing, and tolerances. |
| SAE J1772 | SAE International | North American EV conductive charge coupler standard (Type 1 connector, PWM pilot electrical definitions). |
| IEC 62196-2 | IEC | Plugs, socket-outlets, vehicle connectors, and vehicle inlets (Type 2 Mennekes & Type 1 physical interfaces). |
| IEC 62955 | IEC | Residual Direct Current Detecting Device (RDC-DD) to be used for Mode 3 charging of electric vehicles (6\,mA DC trip). |
| ISO 15118 | ISO / IEC | Road vehicles — Vehicle to grid communication interface (High-Level Communication, Plug & Charge via GreenPHY PLC). |
| OCPP 1.6-J / 2.0.1 | Open Charge Alliance (OCA) | Application protocol for communication between EV charging stations and central management backends. |
| IEC 60664-1 | IEC | Insulation coordination for equipment within low-voltage systems (Creepage and clearance rules). |

4. Documentation Suite Roadmap

The EVSE documentation suite is organized into focused, modular technical guides:

vvdn/evse/ ├── README.md (.docx) # Master architecture, domain overview & standards index ├── evse-low-voltage-controller-working.md (.docx) # Detailed working of the LV controller board, pilot, safety & metering ├── evse-iot-and-communication-subsystem.md (.docx)# IoT gateway, 4G/Wi-Fi/Ethernet, OCPP 1.6J/2.0.1 & DLM └── evse-hardware-schematic-and-interfacing.md (.docx) # Schematics, BOM selection, galvanic isolation & bring-up checklist

1. Low Voltage Controller Board Working & Architecture

Complete internal working of the LV controller board.

Dual-rail power supply generation (± 12\,V bipolar charge pumps).

Control Pilot (CP) op-amp circuit, state transitions (A through F), and diode check mechanics.

Proximity Pilot (PP) resistor decoding and motorized plug lock H-bridge.

RCM 6\,mA DC / 30\,mA AC leakage trip mechanics.

Welded contactor detection and fail-safe interlocks.

Energy metering AFE interfacing with Current Transformers.

2. IoT & Communication Subsystem

Dual-core / Dual-processor architecture (Real-time safety MCU + Linux/FreeRTOS IoT SoC).

Multi-bearer connectivity: 4G LTE Cat-1 modem (AT commands / PPP), Wi-Fi 802.11b/g/n, BLE commissioning, and 10/100 Ethernet.

Complete OCPP 1.6-J and OCPP 2.0.1 message flows (BootNotification, Authorize, StartTransaction, MeterValues, StopTransaction).

Dynamic Load Management (DLM) and solar diversion over RS-485 Modbus RTU.

Dual-bank Over-the-Air (OTA) firmware update architecture.

3. Hardware Schematic Design & Electrical Interfacing

Schematic sub-circuits: CP driver, PP divider, contactor gate driver, motorized lock H-bridge, RCM trigger.

Galvanic isolation barriers: Reinforced insulation, creepage (≥ 6--8\,mm), optocouplers, and digital isolators.

EMC / Surge suppression: MOV, TVS diode, and common-mode filter selections.

Board bring-up checklist, oscilloscope test points, and root-cause troubleshooting matrix.

5. Engineering CLI Utility: tools/evse_calc.py

An automated hardware calculator is provided to compute charging parameters, duty cycles, and safety metrics:

# Calculate allowable AC current and charging power from CP PWM duty cycle: python3 tools/evse_calc.py --mode pwm --duty 53.3 --phase 3 # Sizing required PWM duty cycle for a specific grid current allocation: python3 tools/evse_calc.py --mode current --current 32 --phase 3 --voltage-grid 400 # Decode Control Pilot voltage state: python3 tools/evse_calc.py --mode cp --voltage 6.0 # Decode Proximity Pilot cable assembly resistor: python3 tools/evse_calc.py --mode pp --resistance 220 # Run complete charging session evaluation: python3 tools/evse_calc.py --mode full --current 32 --phase 3 --voltage-grid 400